## IMONI-0047_TTiMBLE26000K004_24_
IMONI ASSEMBLY TEST REPORT
Report No: | iMoni-SRMS-0046
Assembly Sr. No. | TTiMGPE26000K034
DateTime: | 07/08/26 13:05:11
TestLevel: | iMoni Assembly
DeviceIP: | 192.168.0.113 | CPU Sr. No. | Base PCB Sr. No. | Camera Sr. No. | PSU Sr. No.
TotalTests: | 11 | 113 | 55 | 57 | LB/F/26/9134
Sr. No. | TestName | Status | Total Checks | Reason | Remarks
1 | Fan Test | PASSED | 9 | Fan Group 4 turned off successfully
2 | Limit Switch Test | PASSED | 3 | Door alarm went off successfully
3 | Fire Alarm Test | FAILED | 2 | Fire Alarm not turned on
4 | Water Leakage Test | PASSED | 3 | Water Leakage alarm off successfully
5 | EM Lock through Keypad | FAILED | 2 | Door not opened
6 | EM Lock through eMS | FAILED | 3 | Door not closed
7 | Water Logging Test | PASSED | 3 | Water Logging alarm off successfully
8 | Humidity Test | PASSED | 2 | Humidity alarm successfully
9 | Outside Temperature Test | PASSED | 2 | Outside Temperature alarm successfully
10 | Non - Critical Load Test | PASSED | 3 | Door alarm went off successfully
11 | Fan-Fail Test Test | PASSED | 2 | Fan 1 Wire removed successfully
OPERATOR: |  |  | APPROVED BY: