## IMONI-0047_TTiMBLE26000K004_24_
IMONI ASSEMBLY TEST REPORT
Report No: | iMoni-SRMS-0069
Assembly Sr. No. | TTiMGPE26000K038
DateTime: | 07/08/26 17:16:42
TestLevel: | iMoni Assembly
DeviceIP: | 192.168.0.48 | CPU Sr. No. | Base PCB Sr. No. | Camera Sr. No. | PSU Sr. No.
TotalTests: | 8 | 48 | 42 | 52 | LB/F/26/9171
Sr. No. | TestName | Status | Total Checks | Reason | Remarks
1 | Fire Alarm Test | FAILED | 2 | Fire Alarm not turned on
2 | Water Leakage Test | FAILED | 1 | Water Leakage already ON
3 | Water Logging Test | PASSED | 3 | Water Logging alarm off successfully
4 | EM Lock through eMS | PASSED | 3 | Door closed successfully
5 | EM Lock through Keypad | FAILED | 2 | Door not opened
6 | Humidity Test | PASSED | 2 | Humidity alarm successfully
7 | Outside Temperature Test | PASSED | 2 | Outside Temperature alarm successfully
8 | Fan-Fail Test Test | PASSED | 2 | Fan 1 Wire removed successfully
OPERATOR: |  |  | APPROVED BY: