## IMONI-0047_TTiMBLE26000K004_24_
IMONI ASSEMBLY TEST REPORT
Report No: | iMoni-SRMS-0081
Assembly Sr. No. | TTiMGPE26000K047
DateTime: | 08/08/26 16:13:30
TestLevel: | iMoni Assembly
DeviceIP: | 192.168.0.72 | CPU Sr. No. | Base PCB Sr. No. | Camera Sr. No. | PSU Sr. No.
TotalTests: | 10 | 72 | 66 | 62 | LB/F/26/9108
Sr. No. | TestName | Status | Total Checks | Reason | Remarks
1 | Fan Test | PASSED | 9 | Fan Group 4 turned off successfully
2 | Limit Switch Test | PASSED | 3 | Door alarm went off successfully
3 | Fire Alarm Test | PASSED | 3 | Fire alarm turned off successfully
4 | Water Leakage Test | PASSED | 3 | Water Leakage alarm off successfully
5 | Water Logging Test | FAILED | 1 | Water Logging already ON
6 | EM Lock through eMS | PASSED | 3 | Door closed successfully
7 | EM Lock through Keypad | PASSED | 3 | Door closed successfully
8 | Humidity Test | PASSED | 2 | Humidity alarm successfully
9 | Outside Temperature Test | PASSED | 2 | Outside Temperature alarm successfully
10 | Fan-Fail Test Test | PASSED | 2 | Fan 1 Wire removed successfully
OPERATOR: |  |  | APPROVED BY: