## IMONI-0047_TTiMBLE26000K004_24_
IMONI ASSEMBLY TEST REPORT
Report No: | iMoni-SRMS-0065
Assembly Sr. No. | TTiMGPE26000K037
DateTime: | 07/08/26 16:57:55
TestLevel: | iMoni Assembly
DeviceIP: | 192.168.0.96 | CPU Sr. No. | Base PCB Sr. No. | Camera Sr. No. | PSU Sr. No.
TotalTests: | 10 | 96 | 97 | 59 | LB/F/26/9269
Sr. No. | TestName | Status | Total Checks | Reason | Remarks
1 | Fan Test | PASSED | 9 | Fan Group 4 turned off successfully
2 | Limit Switch Test | PASSED | 3 | Door alarm went off successfully
3 | Fire Alarm Test | FAILED | 2 | Fire Alarm not turned on
4 | Water Leakage Test | PASSED | 3 | Water Leakage alarm off successfully
5 | Water Logging Test | PASSED | 3 | Water Logging alarm off successfully
6 | EM Lock through eMS | PASSED | 3 | Door closed successfully
7 | EM Lock through Keypad | FAILED | 3 | Door not closed
8 | Humidity Test | PASSED | 2 | Humidity alarm successfully
9 | Outside Temperature Test | PASSED | 2 | Outside Temperature alarm successfully
10 | Fan-Fail Test Test | FAILED | 2 | Fan 1 wire not removed
OPERATOR: |  |  | APPROVED BY: