## IMONI-0047_TTiMBLE26000K004_24_
IMONI ASSEMBLY TEST REPORT
Report No: | iMoni-SRMS-0079
Assembly Sr. No. | TTiMGPE26000K043
DateTime: | 08/08/26 14:36:27
TestLevel: | iMoni Assembly
DeviceIP: | 192.168.0.91 | CPU Sr. No. | Base PCB Sr. No. | Camera Sr. No. | PSU Sr. No.
TotalTests: | 10 | 91 | 77 | 55 | LB/F/26/9067
Sr. No. | TestName | Status | Total Checks | Reason | Remarks
1 | Fan Test | PASSED | 9 | Fan Group 4 turned off successfully
2 | Limit Switch Test | FAILED | 1 | Door is still open. Close the door first.
3 | Fire Alarm Test | FAILED | 3 | Fire alarm not turned off
4 | Water Leakage Test | PASSED | 3 | Water Leakage alarm off successfully
5 | Water Logging Test | PASSED | 3 | Water Logging alarm off successfully
6 | EM Lock through eMS | PASSED | 3 | Door closed successfully
7 | EM Lock through Keypad | PASSED | 3 | Door closed successfully
8 | Humidity Test | PASSED | 2 | Humidity alarm successfully
9 | Outside Temperature Test | PASSED | 2 | Outside Temperature alarm successfully
10 | Fan-Fail Test Test | PASSED | 2 | Fan 1 Wire removed successfully
OPERATOR: |  |  | APPROVED BY: